## AHU Selection Worksheet
AIR HANDLING UNIT SELECTION WORKSHEET
Project: | [5 empty] | Date: | 2015-08-24 11:57 |  |  |  | LEAVING COIL CONDITIONS
Project No.: | [5 empty] | Calc. By: |  |  |  |  | TEMPDB: | 55 | TEMPWB: | 54.5
Unit Identification Number: |  |  | AHU-1 | [7 empty] | TEMPK: | 285.9378 | TEMPK: | 285.66
Total CFM of Constant Vol. Boxes |  | = | 60000 | [7 empty] | AA: | 0.95531 | AA: | 0.95624 | 2751.52
Total CFM of Variable Vol. Boxes |  | = | 0 | [7 empty] | BB: | 0.044687 | BB: | 0.043758
Diversity of VAV System (%) |  | = | 100% | [7 empty] | CC: | 0.046778 | CC: | 0.045761
CFM of VAV Boxes with Diversity |  | = | 0 | [7 empty] | DD: | 0.48244 | DD: | 0.47241
COOLING COIL DATA |  |  |  |  | AHU STATIC PRESSURE CALCS | [5 empty] | FNGOFF: | 0.2141 | FNGOFF: | 0.21023
Total CFM of Constant Vol. Boxes |  | = | 60000 |  | External Static Pressure | [5 empty] | PSATDB: | 0.2141 | PSATWB: | 0.21023
Total CFM of Variable Vol. Boxes |  | = | 0 |  | Discharge Plenum |  |  | 0.25 |  | 0 |  |  | PPWV: | 0.2076
Total CFM |  | = | 60000 |  | Final Filter |  |  | 1 |  | 0 |  |  | FNRH: | 96.9642
Scheduled AHU CFM |  | = | 60000 |  | Med. Pressure Duct |  |  | 0 |  | 0 |  |  | WLB: | 0.0089085
500 |  | = | 120 |  | Terminal Box |  |  | 0.75 |  | 0 |  |  | WGR: | 62.3593
[5 empty] | Reheat Coil |  |  | 0.25 |  | 0 |  |  | VOLDA: | 12.9801
Total Exhaust CFM |  | = | 10800 |  | Low Pressure S.A. Duct |  |  | 200 |  | 0.16 |  |  | VOLMX: | 13.166
[5 empty] | Volume Damper |  |  | 0.1 |  | 0 |  |  | FNENTH: | 22.8712
Percent Outside Air |  | = | 20% |  | Supply Air Grille |  |  | 0.1 |  | 0
[5 empty] | Return Air Device |  |  | 0.1 |  | 0 | OUTSIDE AIR CONDITIONS
Outside Air |  | = | 12000 |  | Low Pressure R.A. Duct |  |  | 200 |  | 0.16 | TEMPDB: | 98 | TEMPWB: | 74
Scheduled Outside Air CFM |  | = | 12000 |  | Return Air Plenum |  |  | 0.25 |  | 0 | TEMPK: | 309.8267 | TEMPK: | 296.4933
[5 empty] | Pre-Filter |  |  | 0.6 |  | 0 | AA: | 0.88165 | AA: | 0.9213 | 2723.44
Percent Pressurization |  | = | 10% |  | Fire Dampers |  |  | 0.2 |  | 0 | BB: | 0.11835 | BB: | 0.078698
Is pressure between 0% and 10%? |  |  | YES |  | Smoke Dampers |  |  | 0.2 |  | 0 | CC: | 0.13423 | CC: | 0.08542
Return Air CFM |  | = | 48000 |  | Fire/Smoke Dampers |  |  | 0.2 |  | 0 | DD: | 1.2776 | DD: | 0.84961
[5 empty] | O.A. Louvers |  |  | 0.15 |  | 0 | FNGOFF: | 0.8944 | FNGOFF: | 0.41589
| DB |  | WB |  | Outside Air Damper |  |  | 0.1 |  | 0 | PSATDB: | 0.8944 | PSATWB: | 0.41589
Outside Air Temp. = | 98 |  | 74 |  | Outside Air Duct |  |  | 100 |  | 0.08 |  |  | PPWV: | 0.29001
Return Air Temp. = | 75 |  | 62.55 |  | Misc. |  |  |  |  | 0 |  |  | FNRH: | 32.4255
[5 empty] | Misc. |  |  |  |  | 0 |  |  | WLB: | 0.012516
Number of People |  | = | 100 |  | Misc. |  |  |  |  | 0 |  |  | WGR: | 87.6128
0% |  | = | 1681805 |  | Total External Static Pressure |  |  |  |  | 0.4 |  |  | VOLDA: | 14.0639
0% |  | = | 207530 |  | Scheduled External S.P. |  |  |  |  | 0.4 |  |  | VOLMX: | 14.3469
Return Air Temperatire |  | = | 75 |  | Internal Static Pressure | [7 empty] | FNENTH: | 37.3467
Room Delta T |  | = | 20 |  | Pre-Filter |  |  | 0.5 |  | 0
[5 empty] | Mixing Box |  |  | 0.25 |  | 0 | INSIDE AIR CONDITIONS
Fan Location/Type |  | = | Blow Thru |  | Blender/Dampers |  |  | 0.2 |  | 0 | TEMPDB: | 75 | TEMPWB: | 62.55
Motor Heat Gain |  | = | 88089.9937 |  | Pre-Heat Coil |  |  | 0.25 |  | 0 | TEMPK: | 297.0489 | TEMPK: | 290.1322
Temperature Rise |  | = | 1.3538 |  | Cooling Coil |  | 1 | 0.35 |  | 0.35 | AA: | 0.91958 | AA: | 0.9415 | 2739.928
| DB | WB |  | Enthalpy | Reheat Coil |  | 1 | 0.25 |  | 0.25 | BB: | 0.080421 | BB: | 0.058498
Entering Air Temp. = | 80.9538 | 64.84 |  | 28.956 | Diffuser Section |  |  | 0.4 |  | 0 | CC: | 0.087454 | CC: | 0.062133
Leaving Air Temp. = | 55 | 54.5 |  | 22.8712 | Cartridge/Final Filters |  | 1 | 1.2 |  | 1.2 | DD: | 0.86821 | DD: | 0.63154
0% |  | = | 1642900 |  | Discharge Plenum |  |  | 0.15 |  | 0 | FNGOFF: | 0.43005 | FNGOFF: | 0.28058
Tonnage |  | = | 136.9083 |  | Total Internal Static Pressure |  |  |  | = | 1.8 | PSATDB: | 0.43005 | PSATWB: | 0.28058
Leaving Water Temperature |  | = | 58 |  | Total Static Pressure |  |  |  | = | 2.2 |  |  | PPWV: | 0.21506
Entering Water Temperature |  | = | 44 |  | Scheduled Total S.P. |  |  |  | = | 2.2 |  |  | FNRH: | 50.0075
Chilled Water Flow |  | = | 234.7 |  | Brake Horsepower |  |  |  | = | 34.613 |  |  | WLB: | 0.0092331
PRE-HEAT COIL DATA | [12 empty] | WGR: | 64.6316
Outside Air Temperature |  | = | 10 |  | Entering Water Temperature |  |  |  | = | 200 |  |  | VOLDA: | 13.4842
Return Air Temperature |  | = | 75 |  | Leaving Water Temperature |  |  |  | = | 160 |  |  | VOLMX: | 13.6844
Entering Air Temperature |  | = | 62 |  | Leaving Air Temperature |  |  |  | = | 60 |  |  | FNENTH: | 28.1056
Pre-Heat Coil BTU |  | = | Not Required |  | Hot Water Flow (GPM) |  |  |  | = | 0
RE-HEAT (OR HEATING) COIL DATA
Entering (or Outside) Air Temperature |  | = | 62 |  | Entering Water Temperature |  |  |  | = | 200
Leaving Air Temperature |  | = | 100 |  | Leaving Water Temperature |  |  |  | = | 160
Re-Heat (or Heating) Coil BTU |  | = | 2462400 |  | Hot Water Flow (GPM) |  |  |  | = | 123.12
Note on E37: Draw Thru or Blow Thru